## Luzon Outage 12-17 May 2026
Consolidated Outage Data in Luzon Grid - 12 MAY to 18 MAY 2026
Grid | Generation Company | Generating Facility | Generating Unit | Total Outage Capacity (MW) | Actual Outage Occurrence |  | Estimated Resumption |  | Actual Outage Resumption |  | Duration | Reason | Technology | Compliance with Reliability Indices (As of 01 January to 18 May 2026) |  |  | PSA Contracts |  | ASPA |  | Related Groups / Affiliates
[5 empty] | (ERC Reso 04, Ser. 2015) |  |  |  | (ERC Reso 04, Ser. 2015) |  |  | (ERC Reso 04, Ser. 2015) |  | Outage Allowance | Total Accumulated Unplanned Outage Days | Status (positive value means exceeded limits) | Off-taker | Capacity (MW) | Type | Capacity (MW)
[5 empty] | Date Out | Time Out | Date | Time | Date In | Time In
Luzon | VS Gripal Power Corporation | VSGPC BPP | Unit 1 | 6 | 2026-05-18 | 10:37 | 2026-05-25 | 23:59 |  |  | - | Emergency Plant shutdown due to boiler waterwall leakage | Biomass | 7 | 87.31 | 80.31 | N/A | N/A | N/A | N/A | Under Union Equities, Inc. Group with affiliations with the following: 1. Catuiran Hydropower Corporation 2. Grass Gold Renewable Energy Corporation 3. San Jose City 1 Power Corp. 4. VS Gripal Power Corporation
Luzon | CBK Power Company Limited | Botocan HEPP | Unit 2 | 10.498 | 2026-05-17 | 17:01 |  |  | 2026-05-18 | 8:37 | 15.6 | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A | Under Aboitiz Equity Ventures, Inc. Group with affiliations with the following: 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc.
Luzon | Hedcor, Inc. | Lower Labay HEPP | Unit 2 | 0.6 | 2026-05-17 | 10:52 | TBD |  |  |  | - | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A | Under Aboitiz Equity Ventures, Inc. Group with affiliations with the following: 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc.
Luzon | Hedcor, Inc. | Lower Labay HEPP | Unit 2 | 0.6 | 2026-05-17 | 10:38 |  |  | 2026-05-17 | 10:52 | 0.23333 | Electrical Trip (For further investigation) | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | First NatGas Power Corp. | San Gabriel CCPP | Unit 70 | 442.85 | 2026-05-17 | 5:00 |  |  | 2026-05-17 | 12:36 | 7.6 | Shutdown of Batangas-San Lorenzo Line 2 to facilitate correction of hotspot at DS Phase B TPC towards CB at Batangas SS | Combined-Cycle | 7.7 | 5.72 | -1.98 | N/A | N/A | N/A | N/A | Under First Gen Corporation with affiliations with the following: 1. Bac-Man Geothermal Inc. 2. EDC Burgos Wind Power Corporation 3. Energy Development Corporation 4. FGP Corp. 5. FG Bukidnon Power Corporation 6. First Gas Power Corporation 7. First Gen Hydro Power Corporation 8. First Natgas Power Corp. 9. Fresh River Lakes Corp. 10. Green Core Geothermal, Inc. 11. Prime Meridian Powergen Corporation
Luzon | Hedcor, Inc. | FLS HEPP | Unit 1 | 1.2 | 2026-05-17 | 0.12431 |  |  | 2026-05-17 | 19:01 | 16.0333 | Insufficient water supply | Hydroelectric | 6.8 | 132.0146 | 125.2146 | N/A | N/A | N/A | N/A | Under Aboitiz Equity Ventures, Inc. Group with affiliations with the following: 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc.
Luzon | Hedcor, Inc. | FLS HEPP | Unit 4 | 1.2 | 2026-05-17 | 2:43 |  |  | 2026-05-17 | 19:23 | 16.6667 | Insufficient water supply | Hydroelectric | 6.8 | 142.9542 | 136.1542 | N/A | N/A | N/A | N/A
Luzon | One Subic Power Generation Corporation | OSPGC BCFDPP | Unit 4 | 15 | 2026-05-16 | 12:50 |  |  | 2026-05-16 | 19:25 | 6.5833 | Down for repair of cylinder A3 due to water leak on liner wall. | Diesel | 14 | 1.79 | -12.21 | N/A | N/A | DR and RPS | 110 | Under Ayala Corporation with affiliations with the following: 1. Alaminos BESS, Inc. 2. Amihan Renewable Energy Corp. 3. Bataan Solar Energy Inc. 4. Bayog Wind Power Corporation 5. Bulacan Power Generation Corporation 6. CIP II Power Corporation 7. Gigasol3, Inc. 8. Guimaras Wind Corporation 9. Ingrid Power Holdings, Inc. and AERSI 10. Maibarara Geothermal, Inc. 11. Monte Solar Energy Inc. 12. Natures Renewable Energy Devt. Corporation 13. Negros Island Solar Power Inc. 14. North Luzon Renewable Energy Corp. 15. Northwind Power Development Corporation 16. One Subic Power Generation Corp. 17. San Carlos Solar Energy, Inc. 18. Santa Cruz Solar Energy Inc. 19. Sinocalan Solar Power Corp. 20. Solarace1 Energy Corp. 21. South Luzon Thermal Energy Corporation and ACEN Corporation
Luzon | SN Aboitiz Power - Benguet Inc. | Ambuklao HEPP | Unit 2 | 37.5 | 2026-05-16 | 8:05 |  |  | 2026-05-16 | 12:16 | 4.1833 | Annual Preventive Maintenance - To facilitate closing of draft tube gate in support of unit 3 APM | Hydroelectric | - | - | - | IFELCO | 7.5 | RR/ AGC | 23 | Under Aboitiz Equity Ventures, Inc. Group with affiliations with the following: 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc.
Luzon | SN Aboitiz Power - Benguet Inc. | Ambuklao HEPP | Unit 3 | 37.5 | 2026-05-16 | 8:01 | 2026-05-25 | 23:59 |  |  | - | Annual Preventive Maintenance | Hydroelectric | 6.8 | 21.94 | 15.14 | IFELCO | 7.5 | RR/ AGC | 23
Luzon | SN Aboitiz Power - Benguet Inc. | Ambuklao HEPP | Unit 1 | 37.5 | 2026-05-16 | 8:01 |  |  | 2026-05-16 | 17:01 | 9 | Annual Preventive Maintenance -To facilitate closing of draft tube gate in support of unit 3 APM | Hydroelectric | 6.8 | 26.77 | 19.97 | IFELCO | 7.5 | RR/ AGC | 23
Luzon | CBK Power Company Limited | Botocan HEPP | Unit 2 | 10.498 | 2026-05-16 | 3:05 |  |  | 2026-05-16 | 13:10 | 10.0833 | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | SN Aboitiz Power - Benguet Inc. | Binga HEPP | Unit 1 | 35 | 2026-05-16 | 0:03 |  |  | 2026-05-16 | 23:54 | 23.85 | "Hydrological Constraint (Low Reservoir Elevation)" | Hydroelectric | 6.8 | 14.9 | 8.1 | IFELCO | 7.5 | RR and CR / GCM and AGC | 34
Luzon | SN Aboitiz Power - Benguet Inc. | Binga HEPP | Unit 2 | 35 | 2026-05-16 | 0:02 |  |  | 2026-05-16 | 23:54 | 23.8667 | "Hydrological Constraint (Low Reservoir Elevation)" | Hydroelectric | 6.8 | 4.64 | -2.16 | IFELCO | 7.5 | RR and CR / GCM and AGC | 34
Luzon | Therma Mobile, Inc. | TMO M3 Bunker C-Fired DPP | DG 1 | 6 | 2024-11-22 | 10:12 | TBD |  |  |  | - | Damaged Journal bearing | Diesel | 14 | 138 | 124 | N/A | N/A | RR and RPS | 19
Luzon | Therma Mobile, Inc. | TMO M3 Bunker C-Fired DPP | DG 3 | 6 | 2026-04-21 | 22:28 | 2026-07-15 | 23:59 |  |  | - | Sparking observed at Engine Generator | Diesel | 14 | 30.03 | 16.03 | N/A | N/A | RR and RPS | 19
Luzon | Therma Mobile, Inc. | TMO M3 Bunker C-Fired DPP | DG 6 | 6 | 2026-05-15 | 21:20 |  |  | 2026-05-15 | 21:38 | 0.3 | AVR Problem | Diesel | 14 | 3 | -11 | N/A | N/A | RR and RPS | 19
Luzon | CBK Power Company Limited | Kalayaan HEPP | Unit 2 | 175.1 | 2026-05-15 | 18:02 |  |  | 2026-05-16 | 6:30 | 12.4667 | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | CBK Power Company Limited | Kalayaan HEPP | Unit 4 | 175.1 | 2026-05-15 | 18:00 |  |  | 2026-05-16 | 8:20 | 14.3333 | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | CBK Power Company Limited | Botocan HEPP | Unit 1 | 10.498 | 2026-05-15 | 17:02 | TBD |  |  |  | - | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | Therma Mobile, Inc. | TMO M5 Bunker C-Fired DPP | DG 3 | 4 | 2024-12-06 | 0:00 | TBD |  |  |  | - | Damaged Journals and Cylinder Liner blocks | Diesel | 14 | 138 | 124 | N/A | N/A | DR and RPS | 46
Luzon | Therma Mobile, Inc. | TMO M5 Bunker C-Fired DPP | DG 7 | 4 | 2026-05-15 | 16:55 |  |  | 2026-05-15 | 18:55 | 2 | AVR MCB Open Alarm | Diesel | 14 | 2.95 | -11.05 | N/A | N/A | DR and RPS | 46
Luzon | One Subic Power Generation Corporation | OSPGC BCFDPP | Unit 5 | 15 | 2026-05-15 | 14:12 |  |  | 2026-05-15 | 14:48 | 0.6 | Emergency stop due to broken HT water bleeder valve | Diesel | 14 | 1.75 | -12.25 | N/A | N/A | DR and RPS | 46 | Under Ayala Corporation with affiliations with the following: 1. Alaminos BESS, Inc. 2. Amihan Renewable Energy Corp. 3. Bataan Solar Energy Inc. 4. Bayog Wind Power Corporation 5. Bulacan Power Generation Corporation 6. CIP II Power Corporation 7. Gigasol3, Inc. 8. Guimaras Wind Corporation 9. Ingrid Power Holdings, Inc. and AERSI 10. Maibarara Geothermal, Inc. 11. Monte Solar Energy Inc. 12. Natures Renewable Energy Devt. Corporation 13. Negros Island Solar Power Inc. 14. North Luzon Renewable Energy Corp. 15. Northwind Power Development Corporation 16. One Subic Power Generation Corp. 17. San Carlos Solar Energy, Inc. 18. Santa Cruz Solar Energy Inc. 19. Sinocalan Solar Power Corp. 20. Solarace1 Energy Corp. 21. South Luzon Thermal Energy Corporation and ACEN Corporation
Luzon | One Subic Power Generation Corporation | OSPGC BCFDPP | Unit 4 | 15 | 2026-05-15 | 13:09 |  |  | 2026-05-15 | 13:42 | 0.55 | Tripped due to PLC fault | Diesel | - | - | - | N/A | N/A | DR and RPS | 110
Luzon | Therma Mobile, Inc. | TMO M5 Bunker C-Fired DPP | DG 4 | 6 | 2026-05-15 | 10:30 |  |  | 2026-05-15 | 23:54 | 13.4 | Engine High Crankcase Pressure | Diesel | 14 | 3.4 | -10.6 | N/A | N/A | DR and RPS | 46 | Under Aboitiz Equity Ventures, Inc. Group with affiliations with the following: 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc.
Luzon | GNPower Dinginin Ltd. Co. | GNPD CFPP | Unit 1 | 724.965 | 2026-05-15 | 10:15 |  |  | 2026-05-15 | 20:37 | 10.3667 | Turbine Trip due to condenser hot well level high high | Coal-Fired | 16.8 | 6.12 | -10.68 | AURELCO, NEECO I, PELCO III, PRESCO, TARELCO I & II, ZAMECO I & II, PENELCO, BILECO, DORELCO, LEYECO II-V, SOLECO, NORSAMELCO, ESAMELCO, SAMELCO I & II, LUELCO, BATELEC i & II, TEI, ANTECO, ILECO II & III, PELCO II | 553 | CR/GCM | 60
Luzon | Maibarara Geothermal, Inc. | Maibarara GPP | Unit 1 | 20 | 2026-05-15 | 8:35 |  |  | 2026-05-15 | 14:00 | 5.4167 | 52H & 52L Circuit Breaker opened due to Main Transformer Pressure Relief switch wire of its terminal become shorted | Geothermal | 13.7 | 1.92 | -11.78 | N/A | N/A | N/A | N/A | Under Ayala Corporation with affiliations with the following: 1. Alaminos BESS, Inc. 2. Amihan Renewable Energy Corp. 3. Bataan Solar Energy Inc. 4. Bayog Wind Power Corporation 5. Bulacan Power Generation Corporation 6. CIP II Power Corporation 7. Gigasol3, Inc. 8. Guimaras Wind Corporation 9. Ingrid Power Holdings, Inc. and AERSI 10. Maibarara Geothermal, Inc. 11. Monte Solar Energy Inc. 12. Natures Renewable Energy Devt. Corporation 13. Negros Island Solar Power Inc. 14. North Luzon Renewable Energy Corp. 15. Northwind Power Development Corporation 16. One Subic Power Generation Corp. 17. San Carlos Solar Energy, Inc. 18. Santa Cruz Solar Energy Inc. 19. Sinocalan Solar Power Corp. 20. Solarace1 Energy Corp. 21. South Luzon Thermal Energy Corporation and ACEN Corporation
Luzon | Therma Mobile, Inc. | TMO M5 Bunker C-Fired DPP | DG 7 | 6 | 2026-05-15 | 16:55 |  |  | 2026-05-15 | 18:55 | 2 | AVR MCB Open Alarm | Diesel | 14 | 2.95 | -11.05 | N/A | N/A | DR and RPS | 46 | Under Aboitiz Equity Ventures, Inc. Group with affiliations with the following: 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc.
Luzon | Therma Mobile, Inc. | TMO M5 Bunker C-Fired DPP | DG 11 | 6 | 2026-04-26 | 19:22 | 2026-05-20 | 23:59 |  |  | - | Earth fault alarm | Diesel | 14 | 25 | 11 | N/A | N/A | DR and RPS | 46
Luzon | Therma Mobile, Inc. | TMO M5 Bunker C-Fired DPP | DG 5 | 6 | 2026-05-15 | 0:39 |  |  | 2026-05-15 | 0:56 | 0.28333 | Engine overspeed trip | Diesel | 14 | 4.17 | -9.83 | N/A | N/A | DR and RPS | 46
Luzon | SN Aboitiz Power - Benguet Inc. | Ambuklao HEPP | Unit 3 | 37.5 | 2026-05-15 | 0:01 |  |  | 2026-05-16 | 8:00 | 31.9833 | Hydro Constraint (Low Net Head) | Hydroelectric | - | - | - | IFELCO | 7.5 | RR/ AGC | 23
Luzon | SN Aboitiz Power - Benguet Inc. | Ambuklao HEPP | Unit 2 | 37.5 | 2026-05-15 | 0:01 |  |  | 2026-05-16 | 6:15 | 30.2333 | Hydro Constraint (Low Net Head) | Hydroelectric | - | - | - | IFELCO | 7.5 | RR/ AGC | 23
Luzon | SN Aboitiz Power - Benguet Inc. | Ambuklao HEPP | Unit 1 | 37.5 | 2026-05-15 | 0:00 |  |  | 2026-05-16 | 8:00 | 32 | Hydro Constraint (Low Net Head) | Hydroelectric | - | - | - | IFELCO | 7.5 | RR/ AGC | 23
Luzon | SN Aboitiz Power - Magat Inc. | Magat HEPP | Unit 4 | 90 | 2026-05-15 | 0:00 |  |  | 2026-05-15 | 8:01 | 8.0167 | OMC- Limited Allowable Water Release | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | SN Aboitiz Power - Benguet Inc. | Ambuklao HEPP | Unit 3 | 37.5 | 2026-05-14 | 21:38 |  |  | 2026-05-16 | 8:00 | 34.3667 | OMC Hydro Constraint, Low Net head level | Hydroelectric | - | - | - | IFELCO | 7.5 | RR/ AGC | 23
Luzon | Therma Mobile, Inc. | TMO M5 Bunker C-Fired DPP | DG 5 | 4 | 2026-05-14 | 19:56 |  |  | 2026-05-14 | 20:43 | 0.78333 | Engine overspeed trip | Diesel | 14 | 4.17 | -9.83 | N/A | N/A | DR and RPS | 46
Luzon | CBK Power Company Limited | Kalayaan HEPP | Unit 3 | 175.1 | 2026-05-14 | 18:10 |  |  | 2026-05-15 | 3:40 | 9.5 | Insufficient water supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | CBK Power Company Limited | Kalayaan HEPP | Unit 1 | 155.55 | 2026-05-14 | 18:02 |  |  | 2026-05-15 | 4:05 | 10.05 | Insufficient water supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | SN Aboitiz Power - Magat Inc. | Magat HEPP | Unit 2 | 90 | 2026-05-14 | 16:11 |  |  | 2026-05-15 | 0:00 | 7.8167 | OMC- Limited Allowable Water Release | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | SN Aboitiz Power - Magat Inc. | Magat HEPP | Unit 4 | 90 | 2026-05-14 | 13:06 |  |  | 2026-05-15 | 0:00 | 10.9 | OMC- Limited Allowable Water Release | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | Hedcor, Inc. | Lower Labay HEPP | Unit 4 | 0.6 | 2026-05-14 | 12:30 |  |  | 2026-05-17 | 10:52 | 70.3667 | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | Excellent Energy Resources Inc. | Batangas CCPP | Unit 2 | 440 | 2026-05-14 | 8:32 |  |  | 2026-05-15 | 18:23 | 33.85 | Emergency shutdown due to IP FW relief valve tubing detached | Combined-Cycle | 7.7 | 22.1674 | 14.4674 | MERALCO | 1200 | N/A | N/A | Under Aboitiz Equity Ventures, Inc., San Miguel Corporation and Manila Electric Company with affiliations with the following: AEVI 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc. SMC 1. Angat Hydropower Corporation and Metropolitan Waterworks and Sewerage System 2. Excellent Energy Resources, Inc. 3. Isabel Ancillary Services Co. Ltd. and Aggreko Energy Rental Solutions, Inc. 4. Limay Power Inc. 5. Malita Power Inc. 6. Mariveles Power Generation Corp. 7. Masinloc Power Co. Ltd. 8. Petron Corporation 9. San Roque Power Corporation, PSALM, and San Roque Hydropower, Inc. (IPPA) 10. SMGP BESS Power Inc. 11. SMGP Kabankalan Power Co. Ltd. 12. South Premiere Power Corp. 13. Sual Power Inc. MERALCO 1. Excellent Energy Resources, Inc. 2. Cebu Energy Development Corporation 2. Greentech Solar Energy, Inc. 3. Nuevo Solar Energy Corp. 5. Panay Energy Development Corporation 6. Panay Power Corporation 4. PH Renewables, Inc. 5. Powersource First Bulacan Solar Inc. 6. San Buenaventura Power Ltd. Co. 7. Solar Philippines Calatagan Corporation 8. Solar Philippines Tarlac Corporation 9. South Premiere Power Corp. 10. Toledo Power Co.
Luzon | SN Aboitiz Power - Benguet Inc. | Ambuklao HEPP | Unit 2 | 37.5 | 2026-05-14 | 8:02 |  |  | 2026-05-14 | 24:00 | 15.9667 | Hydro Constraint (Low Net Head) | Hydroelectric | - | - | - | IFELCO | 7.5 | RR/ AGC | 23 | Under Aboitiz Equity Ventures, Inc. Group with affiliations with the following: 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc.
Luzon | SN Aboitiz Power - Benguet Inc. | Ambuklao HEPP | Unit 2 | 37.5 | 2026-05-14 | 8:02 |  |  | 2026-05-14 | 24:00 | 15.9667 | Hydro Constraint (Low Net Head) | Hydroelectric | - | - | - | IFELCO | 7.5 | RR/ AGC | 23
Luzon | Excellent Energy Resources Inc. | Batangas CCPP | Unit 3 | 440 | 2026-05-14 | 7:35 |  |  | 2026-05-15 | 16:17 | 32.7 | Unit 3 remains on shutdown due to CWP line breather leak | Combined-Cycle | 7.7 | 11.9632 | 4.2632 | MERALCO | 1200 | N/A | N/A | Under Aboitiz Equity Ventures, Inc., San Miguel Corporation and Manila Electric Company with affiliations with the following: AEVI 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc. SMC 1. Angat Hydropower Corporation and Metropolitan Waterworks and Sewerage System 2. Excellent Energy Resources, Inc. 3. Isabel Ancillary Services Co. Ltd. and Aggreko Energy Rental Solutions, Inc. 4. Limay Power Inc. 5. Malita Power Inc. 6. Mariveles Power Generation Corp. 7. Masinloc Power Co. Ltd. 8. Petron Corporation 9. San Roque Power Corporation, PSALM, and San Roque Hydropower, Inc. (IPPA) 10. SMGP BESS Power Inc. 11. SMGP Kabankalan Power Co. Ltd. 12. South Premiere Power Corp. 13. Sual Power Inc. MERALCO 1. Excellent Energy Resources, Inc. 2. Cebu Energy Development Corporation 2. Greentech Solar Energy, Inc. 3. Nuevo Solar Energy Corp. 5. Panay Energy Development Corporation 6. Panay Power Corporation 4. PH Renewables, Inc. 5. Powersource First Bulacan Solar Inc. 6. San Buenaventura Power Ltd. Co. 7. Solar Philippines Calatagan Corporation 8. Solar Philippines Tarlac Corporation 9. South Premiere Power Corp. 10. Toledo Power Co.
Luzon | SN Aboitiz Power - Magat Inc. | Magat HEPP | Unit 2 | 90 | 2026-05-14 | 6:02 |  |  | 2026-05-14 | 10:01 | 3.9833 | OMC- Limited Allowable Water Release | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A | Under Aboitiz Equity Ventures, Inc. Group with affiliations with the following: 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc.
Luzon | SN Aboitiz Power - Benguet Inc. | Binga HEPP | Unit 3 | 35 | 2026-05-14 | 2:01 |  |  | 2026-05-17 | 23:52 | 93.85 | OMC below operating level | Hydroelectric | - | - | - | IFELCO | 7.5 | RR and CR / GCM and AGC | 34
Luzon | SN Aboitiz Power - Benguet Inc. | Binga HEPP | Unit 3 | 35 | 2026-05-14 | 1:13 |  |  | 2026-05-14 | 2:01 | 0.8 | Unit tripped to start due Lower Guide Bearing Segment High Temp | Hydroelectric | 6.8 | 20 | 13.2 | IFELCO | 7.5 | RR and CR / GCM and AGC | 34
Luzon | SN Aboitiz Power - Benguet Inc. | Ambuklao HEPP | Unit 3 | 37.5 | 2026-05-14 | 0:02 |  |  | 2026-05-14 | 7:55 | 7.8833 | OMC Hydro Constraint, Low net head level | Hydroelectric | - | - | - | IFELCO | 7.5 | RR/ AGC | 23
Luzon | SN Aboitiz Power - Benguet Inc. | Binga HEPP | Unit 1 | 35 | 2026-05-14 | 0:00 |  |  | 2026-05-14 | 1:38 | 1.6333 | "OMC outage due to Hydrological Constraint (Low Reservoir Elevation)" | Hydroelectric | - | - | - | IFELCO | 7.5 | RR and CR / GCM and AGC | 34
Luzon | SN Aboitiz Power - Magat Inc. | Magat HEPP | Unit 4 | 90 | 2026-05-14 | 0:00 |  |  | 2026-05-14 | 12:46 | 12.7667 | OMC- Limited Allowable Water Release | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | South Premiere Power Corp. | Ilijan CCPP | Block 1 | 718.25 | 2026-05-13 | 21:51 |  |  | 2026-05-17 | 22:30 | 96.65 | On outage due to Auxiliary Boiler tube leak | Combined-Cycle | 7.7 | 5.2 | -2.5 | MERALCO | 1200 | N/A | N/A | Under Aboitiz Equity Ventures, Inc., San Miguel Corporation and Manila Electric Company with affiliations with the following: AEVI 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc. SMC 1. Angat Hydropower Corporation and Metropolitan Waterworks and Sewerage System 2. Excellent Energy Resources, Inc. 3. Isabel Ancillary Services Co. Ltd. and Aggreko Energy Rental Solutions, Inc. 4. Limay Power Inc. 5. Malita Power Inc. 6. Mariveles Power Generation Corp. 7. Masinloc Power Co. Ltd. 8. Petron Corporation 9. San Roque Power Corporation, PSALM, and San Roque Hydropower, Inc. (IPPA) 10. SMGP BESS Power Inc. 11. SMGP Kabankalan Power Co. Ltd. 12. South Premiere Power Corp. 13. Sual Power Inc. MERALCO 1. Excellent Energy Resources, Inc. 2. Cebu Energy Development Corporation 2. Greentech Solar Energy, Inc. 3. Nuevo Solar Energy Corp. 5. Panay Energy Development Corporation 6. Panay Power Corporation 4. PH Renewables, Inc. 5. Powersource First Bulacan Solar Inc. 6. San Buenaventura Power Ltd. Co. 7. Solar Philippines Calatagan Corporation 8. Solar Philippines Tarlac Corporation 9. South Premiere Power Corp. 10. Toledo Power Co.
Luzon | South Premiere Power Corp. | Ilijan CCPP | Block 2 | 718.25 | 2026-05-13 | 21:51 |  |  | 2026-05-18 | 6:21 | 104.5 | On outage due to Auxiliary Boiler tube leak | Combined-Cycle | 7.7 | 115.79 | 108.09 | MERALCO | 1200 | N/A | N/A
Luzon | SN Aboitiz Power - Benguet Inc. | Ambuklao HEPP | Unit 2 | 37.5 | 2026-05-13 | 21:44 |  |  | 2026-05-13 | 23:48 | 2.0667 | Hydro Constraint (Low Net Head) | Hydroelectric | - | - | - | IFELCO | 7.5 | RR/ AGC | 23 | Under Aboitiz Equity Ventures, Inc. Group with affiliations with the following: 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc.
Luzon | CBK Power Company Limited | Kalayaan HEPP | Unit 2 | 155.55 | 2026-05-13 | 16:00 |  |  | 2026-05-15 | 8:16 | 40.2667 | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | CBK Power Company Limited | Kalayaan HEPP | Unit 4 | 175.1 | 2026-05-13 | 16:00 |  |  | 2026-05-15 | 8:37 | 40.6167 | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | SN Aboitiz Power - Benguet Inc. | Ambuklao HEPP | Unit 2 | 37.5 | 2026-05-13 | 8:02 |  |  | 2026-05-13 | 15:01 | 6.9833 | To facilitate the closing and opening of draft tube gates to support APM activities of unit 1 | Hydroelectric | 6.8 | 25.65 | 18.85 | IFELCO | 7.5 | RR/ AGC | 23 | Under Aboitiz Equity Ventures, Inc. Group with affiliations with the following: 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc.
Luzon | Bac-Man Geothermal Inc. | Bac-Man 2 GPP | Unit 3 | 20 | 2026-05-13 | 6:36 |  |  | 2026-05-13 | 21:03 | 14.45 | Due to Bently Nevada trip caused by grid under frequency | Geothermal | 13.7 | 2.21 | -11.49 | N/A | N/A | N/A | N/A | Under First Gen Corporation with affiliations with the following: 1. Bac-Man Geothermal Inc. 2. EDC Burgos Wind Power Corporation 3. Energy Development Corporation 4. FGP Corp. 5. FG Bukidnon Power Corporation 6. First Gas Power Corporation 7. First Gen Hydro Power Corporation 8. First Natgas Power Corp. 9. Fresh River Lakes Corp. 10. Green Core Geothermal, Inc. 11. Prime Meridian Powergen Corporation
Luzon | Masinloc Power Co., Ltd. | Masinloc CFTPP | Unit 3 | 335 | 2026-05-13 | 6:34 |  |  | 2026-05-13 | 16:21 | 9.7833 | Turbine Tripped due to turbine protection actuated | Coal-Fired | 16.8 | 2.74 | -14.06 | BATELEC I, CASURECO II,CELCOR-BL, CELCOR-MM, LUECO, SFELAPCO, ABRECO, INEC, ISECO, KAELCO, LUELCO, MOPRECO, PANELCO I, PANELCO III & SAJELCO | 336.84 | N/A | N/A | Under San Miguel Corporation with affiliations with the following: 1. Angat Hydropower Corporation and Metropolitan Waterworks and Sewerage System 2. Excellent Energy Resources, Inc. 3. Isabel Ancillary Services Co. Ltd. and Aggreko Energy Rental Solutions, Inc. 4. Limay Power Inc. 5. Malita Power Inc. 6. Mariveles Power Generation Corp. 7. Masinloc Power Co. Ltd. 8. Petron Corporation 9. San Roque Power Corporation, PSALM, and San Roque Hydropower, Inc. (IPPA) 10. SMGP BESS Power Inc. 11. SMGP Kabankalan Power Co. Ltd. 12. South Premiere Power Corp. 13. Sual Power Inc.
Luzon | South Premiere Power Corp. | Ilijan CCPP | Block 1 | 718.25 | 2026-05-13 | 6:30 |  |  | 2026-05-13 | 21:51 | 15.35 | All units tripped due to opening of GCBs at Ilijan Switchyard following Tayabas-Ilijan 500kV Line Tripping | Combined-Cycle | - | - | - | MERALCO | 1200 | N/A | N/A | Under Aboitiz Equity Ventures, Inc., San Miguel Corporation and Manila Electric Company with affiliations with the following: AEVI 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc. SMC 1. Angat Hydropower Corporation and Metropolitan Waterworks and Sewerage System 2. Excellent Energy Resources, Inc. 3. Isabel Ancillary Services Co. Ltd. and Aggreko Energy Rental Solutions, Inc. 4. Limay Power Inc. 5. Malita Power Inc. 6. Mariveles Power Generation Corp. 7. Masinloc Power Co. Ltd. 8. Petron Corporation 9. San Roque Power Corporation, PSALM, and San Roque Hydropower, Inc. (IPPA) 10. SMGP BESS Power Inc. 11. SMGP Kabankalan Power Co. Ltd. 12. South Premiere Power Corp. 13. Sual Power Inc. MERALCO 1. Excellent Energy Resources, Inc. 2. Cebu Energy Development Corporation 2. Greentech Solar Energy, Inc. 3. Nuevo Solar Energy Corp. 5. Panay Energy Development Corporation 6. Panay Power Corporation 4. PH Renewables, Inc. 5. Powersource First Bulacan Solar Inc. 6. San Buenaventura Power Ltd. Co. 7. Solar Philippines Calatagan Corporation 8. Solar Philippines Tarlac Corporation 9. South Premiere Power Corp. 10. Toledo Power Co.
Luzon | South Premiere Power Corp. | Ilijan CCPP | Block 2 | 718.25 | 2026-05-13 | 6:30 |  |  | 2026-05-13 | 21:51 | 15.35 | All units tripped due to opening of GCBs at Ilijan Switchyard following Tayabas-Ilijan 500kV Line Tripping | Combined-Cycle | - | - | - | MERALCO | 1200 | N/A | N/A
Luzon | Excellent Energy Resources Inc. | Batangas CCPP | Unit 1 | 440 | 2026-05-13 | 6:30 |  |  | 2026-05-13 | 21:51 | 15.35 | All units tripped due to opening of GCBs at Ilijan Switchyard following Tayabas-Ilijan 500kV Line Tripping | Combined-Cycle | 7.7 | 83.6417 | 75.9417 | MERALCO | 1200 | N/A | N/A
Luzon | Excellent Energy Resources Inc. | Batangas CCPP | Unit 2 | 440 | 2026-05-13 | 6:30 |  |  | 2026-05-14 | 7:31 | 25.0167 | All units tripped due to opening of GCBs at Ilijan Switchyard following Tayabas-Ilijan 500kV Line Tripping | Combined-Cycle | 7.7 | 22.1674 | 14.4674 | MERALCO | 1200 | N/A | N/A
Luzon | Excellent Energy Resources Inc. | Batangas CCPP | Unit 3 | 440 | 2026-05-13 | 6:30 |  |  | 2026-05-13 | 21:51 | 15.35 | All units tripped due to opening of GCBs at Ilijan Switchyard following Tayabas-Ilijan 500kV Line Tripping | Combined-Cycle | 7.7 | 11.9632 | 4.2632 | MERALCO | 1200 | N/A | N/A
Luzon | Bac-Man Geothermal Inc. | Palayan Binary GPP | Unit 1 | 35.7 | 2026-05-13 | 6:30 |  |  | 2026-05-15 | 16:43 | 58.2167 | Unit auto-tripped following a system grid disturbance | Geothermal | 13.7 | 42.22 | 28.52 | BATELEC II, CAGELCO | 75 | N/A | N/A | Under First Gen Corporation with affiliations with the following: 1. Bac-Man Geothermal Inc. 2. EDC Burgos Wind Power Corporation 3. Energy Development Corporation 4. FGP Corp. 5. FG Bukidnon Power Corporation 6. First Gas Power Corporation 7. First Gen Hydro Power Corporation 8. First Natgas Power Corp. 9. Fresh River Lakes Corp. 10. Green Core Geothermal, Inc. 11. Prime Meridian Powergen Corporation
Luzon | SN Aboitiz Power - Magat Inc. | Magat HEPP | Unit 2 | 90 | 2026-05-13 | 4:06 |  |  | 2026-05-13 | 10:03 | 5.95 | Low water elevation | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A | Under Aboitiz Equity Ventures, Inc. Group with affiliations with the following: 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc.
Luzon | SN Aboitiz Power - Benguet Inc. | Binga HEPP | Unit 3 | 35 | 2026-05-13 | 0:11 |  |  | 2026-05-13 | 23:49 | 23.6333 | "OMC outage due to Hydrological Constraint (Low Reservoir Elevation)" | Hydroelectric | - | - | - | IFELCO | 7.5 | RR and CR / GCM and AGC | 34
Luzon | SN Aboitiz Power - Magat Inc. | Magat HEPP | Unit 4 | 90 | 2026-05-13 | 0:09 |  |  | 2026-05-13 | 12:01 | 11.8667 | Low water elevation | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | SN Aboitiz Power - Benguet Inc. | Binga HEPP | Unit 3 | 35 | 2026-05-12 | 22:01 |  |  | 2026-05-13 | 0:11 | 2.1667 | Unit failed to start due cooling water feedback relay failure. | Hydroelectric | - | - | - | IFELCO | 7.5 | RR and CR / GCM and AGC | 34
Luzon | SN Aboitiz Power - Benguet Inc. | Ambuklao HEPP | Unit 2 | 37.5 | 2026-05-12 | 8:04 |  |  | 2026-05-12 | 18:22 | 10.3 | Hydro Constraint (Low Net Head) | Hydroelectric | - | - | - | IFELCO | 7.5 | RR/ AGC | 23
Luzon | SN Aboitiz Power - Magat Inc. | Magat HEPP | Unit 2 | 90 | 2026-05-12 | 0:00 |  |  | 2026-05-12 | 13:02 | 13.0333 | OMC- Limited Allowable Water Release | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | SN Aboitiz Power - Magat Inc. | Magat HEPP | Unit 4 | 90 | 2026-05-12 | 0:00 |  |  | 2026-05-12 | 19:06 | 19.1 | OMC- Limited Allowable Water Release | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | SN Aboitiz Power - Benguet Inc. | Binga HEPP | Unit 3 | 35 | 2026-05-11 | 20:48 |  |  | 2026-05-12 | 22:01 | 25.2167 | "OMC outage due to Hydrological Constraint (Low Reservoir Elevation)" | Hydroelectric | - | - | - | IFELCO | 7.5 | RR and CR / GCM and AGC | 34
Luzon | SN Aboitiz Power - Benguet Inc. | Binga HEPP | Unit 2 | 35 | 2026-05-11 | 20:13 |  |  | 2026-05-12 | 21:50 | 25.6167 | "OMC outage due to Hydrological Constraint (Low Reservoir Elevation)" | Hydroelectric | - | - | - | IFELCO | 7.5 | RR and CR / GCM and AGC | 34
Luzon | SN Aboitiz Power - Magat Inc. | Magat HEPP | Unit 3 | 90 | 2026-05-11 | 19:33 |  |  | 2026-05-11 | 23:59 | 4.4333 | OMC- Limited Allowable Water Release | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | CBK Power Company Limited | Botocan HEPP | Unit 1 | 10.498 | 2026-05-11 | 0:03 |  |  | 2026-05-15 | 17:02 | 112.9833 | To conduct Semi-annual preventive maintenance | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | CBK Power Company Limited | Botocan HEPP | Unit 2 | 10.498 | 2026-05-11 | 0:03 |  |  | 2026-05-15 | 17:02 | 112.9833 | To conduct Semi-annual preventive maintenance | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | Mariveles Power Generation Corp | MPGC CFPP | Unit 4 | 150 | 2026-05-10 | 3:04 |  |  | 2026-05-15 | 3:11 | 120.1167 | Master fuel trip due to furnace pressure high high high | Coal-Fired | 16.9 | 11.59 | -5.31 | MERALCO | 300 | N/A | N/A | Under San Miguel Corporation with affiliations with the following: 1. Angat Hydropower Corporation and Metropolitan Waterworks and Sewerage System 2. Excellent Energy Resources, Inc. 3. Isabel Ancillary Services Co. Ltd. and Aggreko Energy Rental Solutions, Inc. 4. Limay Power Inc. 5. Malita Power Inc. 6. Mariveles Power Generation Corp. 7. Masinloc Power Co. Ltd. 8. Petron Corporation 9. San Roque Power Corporation, PSALM, and San Roque Hydropower, Inc. (IPPA) 10. SMGP BESS Power Inc. 11. SMGP Kabankalan Power Co. Ltd. 12. South Premiere Power Corp. 13. Sual Power Inc.
Luzon | SN Aboitiz Power - Benguet Inc. | Ambuklao HEPP | Unit 1 | 37.5 | 2026-05-05 | 8:01 |  |  | 2026-05-15 | 0:00 | 231.9833 | Annual Preventive Maintenance | Hydroelectric | - | - | - | IFELCO | 7.5 | RR/ AGC | 23 | Under Aboitiz Equity Ventures, Inc. Group with affiliations with the following: 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc.
Luzon | San Roque Power Corporation | San Roque HEPP | Unit 2 | 127.5 | 2026-05-04 | 0:01 |  |  | 2026-05-15 | 24:00 | 287.9833 | Unit 2 Annual Inspection according to CY2026 GOP | Hydroelectric | 6.8 | 0.54 | -6.26 | N/A | N/A | N/A | N/A | Under San Miguel Corporation with affiliations with the following: 1. Angat Hydropower Corporation and Metropolitan Waterworks and Sewerage System 2. Excellent Energy Resources, Inc. 3. Isabel Ancillary Services Co. Ltd. and Aggreko Energy Rental Solutions, Inc. 4. Limay Power Inc. 5. Malita Power Inc. 6. Mariveles Power Generation Corp. 7. Masinloc Power Co. Ltd. 8. Petron Corporation 9. San Roque Power Corporation, PSALM, and San Roque Hydropower, Inc. (IPPA) 10. SMGP BESS Power Inc. 11. SMGP Kabankalan Power Co. Ltd. 12. South Premiere Power Corp. 13. Sual Power Inc.
Luzon | SN Aboitiz Power - Benguet Inc. | Binga HEPP | Unit 4 | 35 | 2026-05-04 | 0:01 |  |  | 2026-05-17 | 23:52 | 335.85 | OMC Low net head / water level | Hydroelectric | 6.8 | 29.43 | 22.63 | IFELCO | 7.5 | RR and CR / GCM and AGC | 34 | Under Aboitiz Equity Ventures, Inc. Group with affiliations with the following: 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc.
Luzon | Hedcor, Inc. | Sal-Angan HEPP | Unit 1 | 0.6 | 2026-04-22 | 16:41 | TBD |  |  |  | - | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | Hedcor, Inc. | Sal-Angan HEPP | Unit 2 | 0.6 | 2026-04-22 | 16:41 | TBD |  |  |  | - | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | Hedcor, Inc. | Sal-Angan HEPP | Unit 3 | 0.6 | 2026-04-22 | 16:41 | TBD |  |  |  | - | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | Hedcor, Inc. | Sal-Angan HEPP | Unit 4 | 0.6 | 2026-04-22 | 16:41 | TBD |  |  |  | - | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | NIA Baligatan Hydroelectric Power Plant | Baligatan HEPP | Unit 1 | 6 | 2026-03-22 | 5:07 | 2026-06-01 | 0:00 |  |  | - | Suspension due to Irrigation Diversion Requirement (IDR) Cut-off | Hydroelectric | 6.8 | 0.02 | -6.78 | N/A | N/A | N/A | N/A | No affiliations; Under a Government Controlled arrangement
Luzon | Republic Cement & Building Materials, Inc. | Batangas DPP | DG 1 | 5.5 | 2026-03-18 | 20:15 | 2026-06-30 | 0:01 |  |  | - | Heavy water leak at the turbocharger leak-off line B-bank | Diesel | 14 | 98.71 | 84.71 | N/A | N/A | N/A | N/A | Under Aboitiz Equity Ventures, Inc. Group with affiliations with the following: 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc.
Luzon | Hedcor, Inc. | La Trinidad HEPP | Unit 1 | 10.2 | 2026-03-13 | 13:51 | 2026-06-01 | 0:00 |  |  | - | Insufficient Water Supply | Hydroelectric | 6.8 | 115.79 | 108.99 | N/A | N/A | N/A | N/A
Luzon | Hedcor, Inc. | La Trinidad HEPP | Unit 2 | 10.2 | 2026-03-13 | 13:51 | 2026-06-01 | 0:00 |  |  | - | Insufficient Water Supply | Hydroelectric | 6.8 | 118.27 | 111.47 | N/A | N/A | N/A | N/A
Luzon | Hedcor, Inc. | Irisan 1 HEPP | Unit 1 | 3.89 | 2026-03-13 | 13:38 | 2026-06-01 | 0:00 |  |  | - | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | Hedcor, Inc. | Irisan 3 HEPP | Unit 1 | 0.4 | 2026-03-13 | 13:38 | 2026-06-01 | 0:00 |  |  | - | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | Hedcor, Inc. | Irisan 3 HEPP | Unit 2 | 0.4 | 2026-03-13 | 13:38 | 2026-06-01 | 0:00 |  |  | - | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | Hedcor, Inc. | Irisan 3 HEPP | Unit 3 | 0.4 | 2026-03-13 | 13:38 | 2026-06-01 | 0:00 |  |  | - | Insufficient Water Supply | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Luzon | Belgrove Power Corporation | Malaya OFTPP | Unit 2 | 350 | 2024-07-24 | 21:24 |  |  |  |  | - | Tripped due to loss prime of CWP | Oil-Fired Thermal | 27.8 | 138 | 110.2 | N/A | N/A | N/A | N/A | Under One Power Systems Holdings, Inc. with affiliations with the following: 1. Alterpower Digos Solar, Inc. 2. Fort Pilar Energy, Inc.
Luzon | Belgrove Power Corporation | Malaya OFTPP | Unit 1 | 300 | 2019-05-03 | 18:21 |  |  |  |  | - | Declared unavailable due to motorization of unit generator caused by the non-opening of phase B of PCB 8-05CB08MAL (from CDOR) | Oil-Fired Thermal | - | - | - | N/A | N/A | N/A | N/A
Note on H6: ERC IED GenCo: As per Ma'am Rowena of VSPGC
Note on H15: As per Sir Willard Madarang
Note on D61: Frank James: Not identified in the SIN
Note on Q63: Jean Rose E. Villagracia: As of 13 May 2026 (SER)
Note on Q70: Jean Rose E. Villagracia: As of 15 May 2026 (SER)
Note on H91: ENGR. JANRECK CRIBE: Francis Francisco
Note on H93: ENGR. JANRECK CRIBE: Charles Calisen
Note on H94: ENGR. JANRECK CRIBE: Charles Calisen
Note on H95: ENGR. JANRECK CRIBE: Charles Calisen
Note on H96: ENGR. JANRECK CRIBE: Charles Calisen
Note on H97: ENGR. JANRECK CRIBE: Charles Calisen
Note on C100: ERC Outage Reports: No letter for decommissioning

## Visayas Outage May 12-17, 2026
Consolidated Outage Data in Visayas Grid - 12 MAY to 18 MAY 2026
Grid | Generation Company | Generating Facility | Generating Unit | Total Outage Capacity (MW) | Actual Outage Occurrence |  | Estimated Resumption |  | Actual Outage Resumption |  | Duration | Reason | Technology | Compliance with Reliability Indices (As of 01 January to 18 May 2026) |  |  | PSA Contracts |  | ASPA |  | Related Groups / Affiliates
[5 empty] | (ERC Reso 04, Ser. 2015) |  |  |  | (ERC Reso 04, Ser. 2015) |  |  | (ERC Reso 04, Ser. 2015) |  | Outage Allowance | Total Accumulated UO Days | Status | Off-taker | Capacity | Type | Capacity
[5 empty] | Date Out | Time Out | Date | Time | Date In | Time In
Visayas | Central Azucarera De San Antonio, Inc. | CASA BPP | Unit 1 | 15 | 2026-05-17 | 21:22 |  |  | 2026-05-17 | 21:27 | 0.083333 | Disturbance at Distribution Utility | Biomass | 7 | 3.316 | -3.684 | N/A | N/A | N/A | N/A | Under Chan Group with affiliations with the following: 1. Central Azucarera De Bais, Inc. 2. Central Azucarera De San Antonio, Inc.
Visayas | Central Negros Power Reliability, Inc. | CENPRI Bunker C-Fired DPP | Unit 1 | 5 | 2026-05-17 | 16:13 |  |  | 2026-05-17 | 16:46 | 0.55 | DG Set unload due to circuit breaker charging motor failure | Diesel | 14 | 3.0181 | -10.9819 | NEPC | 18.9 | N/A | N/A | Under Energreen Power Inter-Island Corp. with affiliations with the following: 1. Central Negros Power Reliability, Inc. 2. Mindoro Harvest Energy Co. Inc.
Visayas | First Farmers Holding Corporation | FFHC BPP | Unit 1 | 21.76 | 2026-05-17 | 5:52 |  |  | 2026-05-17 | 9:09 | 3.2833 | Scheduled shutdown of Cadiz-Victorias-Talisay 69kV Transmission Line as per NEPC request | Biomass | 7 | 30.26 | 23.26 | N/A | N/A | N/A | N/A | No other affiliations; Owned majority by Individuals
Visayas | Central Azucarera de Bais, Inc. | CABI BPP | Unit 1 | 20 | 2026-05-17 | 5:50 |  |  | 2026-05-17 | 18:30 | 12.6667 | Zero export due to NGCP Maintenance Shutdown | Biomass | 7 | 9.8042 | 2.8042 | N/A | N/A | N/A | N/A | Under Chan Group with affiliations with the following: 1. Central Azucarera De Bais, Inc. 2. Central Azucarera De San Antonio, Inc.
Visayas | Bohol I Electric Cooperative, Inc. | Sevilla MHEPP | Unit 2 | 1.328 | 2026-05-17 | 1:58 | TBD |  |  |  | - | Low water level | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A | No affiliations; Under a Cooperative Arrangement
Visayas | Bohol I Electric Cooperative, Inc. | Sevilla MHEPP | Unit 1 | 1.328 | 2026-05-17 | 1:58 | TBD |  |  |  | - | Low water level | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Visayas | Panay Energy Development Corporation | PEDC CFTPP | Unit 2 | 83.7 | 2026-05-17 | 0:28 |  |  | 2026-05-17 | 4:24 | 3.9333 | Emergency Maintenance Shutdown | Coal-Fired | 16.9 | 1.9986 | -14.9014 | ILECO II PECO AKELCO | 10 MW 65 MW 12 MW | N/A | N/A | Under Manila Electric Company with affiliations with the following: 1. Excellent Energy Resources, Inc. 2. Cebu Energy Development Corporation 2. Greentech Solar Energy, Inc. 3. Nuevo Solar Energy Corp. 5. Panay Energy Development Corporation 6. Panay Power Corporation 4. PH Renewables, Inc. 5. Powersource First Bulacan Solar Inc. 6. San Buenaventura Power Ltd. Co. 7. Solar Philippines Calatagan Corporation 8. Solar Philippines Tarlac Corporation 9. South Premiere Power Corp. 10. Toledo Power Co.
Visayas | SPC Island Power Corporation | Panay 3 DPP | Golf | 15 | 2026-05-16 | 23:42 |  |  | 2026-05-17 | 7:10 | 7.4667 | Manually shutdown unit Golf due to excessive water leak between engine frame and liner of cylinder | Diesel | 14 | 2.56 | -11.44 | N/A | N/A | N/A | N/A | Under Korea Electric Power Corporation with affiliations with the following: 1. KEPCO SPC Power Corporation 2. SPC Island Power Corporation 3. SPC Power Corporation
Visayas | Victorias Milling Company Inc. | VMCI BPP | Unit 3 | 40 | 2026-05-16 | 23:15 | 2026-05-31 | 0:00 |  |  | - | No milling operation/insufficient cane supply | Biomass | 7 | 21.08 | 14.08 | N/A | N/A | N/A | N/A | Under LT Group, Inc. with affiliations with the following: 1. Absolut Distillers, Inc. 2. Victorias Milling Company, Inc.
Visayas | Meridian Power Inc. | MPI Bunker C-Fired DPP | DG 2 | 7.059 | 2026-05-16 | 19:35 | 2026-05-19 | 20:00 |  |  | - | Oil Mist Concentration Shutdown | Diesel | 14 | 2.5646 | -11.4354 | VECO | 70 MW | N/A | N/A | Under Vivant Corporation with affiliations with the following: 1. 1590 Energy Corp. 2. Bukidnonpower Corporation 3. Calamian Islands Power Corp. 4. Cebu Energy Development Corporation 5. Delta P, Inc. and AERSI 6. Isla Norte Power Corporation 7. Meridian Power Inc. 8. Minergy Power Corporation 9. North Bukidnonpower Corporation
Visayas | SPC Island Power Corporation | Bohol DPP | Unit 3 | 5.52 | 2026-05-16 | 19:02 |  |  | 2026-05-16 | 20:30 | 1.4667 | Forced Cut out due to observed heavy smoke at cylinder no. 8 | Diesel | 14 | 3.3535 | -10.6465 | BLCI | 16 MW | N/A | N/A | Under Korea Electric Power Corporation with affiliations with the following: 1. KEPCO SPC Power Corporation 2. SPC Island Power Corporation 3. SPC Power Corporation
Visayas | Sunwest Water and Electric Company 2, Inc. | Villasiga HEPP | Unit 2 | 3.6 | 2026-05-16 | 14:00 |  |  | 2026-05-18 | 8:00 | 42 | Shutdown due to low water yield | Hydroelectric | - | - | - | ANTECO | 8 MW | N/A | N/A | Under Sunwest Group Holding Company, Inc. with affiliations with the following: 1. Sunwest Water and Electric Company 2, Inc. 2. Sunwest Water and Electric Co. (SUWECO), Inc. 3. SUWECO Tablas Energy Corporation
Visayas | Bohol I Electric Cooperative, Inc. | Sevilla MHEPP | Unit 2 | 1.328 | 2026-05-16 | 13:55 |  |  | 2026-05-16 | 15:20 | 1.4167 | Low water level | Hydroelectric | - | - | - | BOHECO I | 1 MW | N/A | N/A | No affiliations; Under a Cooperative Arrangement
Visayas | Central Azucarera De San Antonio, Inc. | CASA BPP | Unit 1 | 15 | 2026-05-16 | 7:20 |  |  | 2026-05-16 | 7:26 | 0.1 | Disturbance at Distribution Utility | Biomass | 7 | 3.316 | -3.684 | N/A | N/A | N/A | N/A | Under Chan Group with affiliations with the following: 1. Central Azucarera De Bais, Inc. 2. Central Azucarera De San Antonio, Inc.
Visayas | Bohol I Electric Cooperative, Inc. | Sevilla MHEPP | Unit 1 | 1.328 | 2026-05-16 | 1:30 |  |  | 2026-05-17 | 11:02 | 33.5333 | Low water level | Hydroelectric | - | - | - | BOHECO I | 1 MW | N/A | N/A | No affiliations; Under a Cooperative Arrangement
Visayas | Green Core Geothermal, Inc. | Tongonan GPP | Unit 3 | 41 | 2026-05-16 | 0:30 |  |  | 2026-05-18 | 2:21 | 49.85 | Unit on emergency shutdown to carry out an inspection and repair of its turbine gland sealing lines | Geothermal | 13.7 | 10.3 | -3.4 | ILECO I CAPELCO | 18 MW 12 MW | N/A | N/A | Under First Gen Corporation with affiliations with the following: 1. Bac-Man Geothermal Inc. 2. EDC Burgos Wind Power Corporation 3. Energy Development Corporation 4. FGP Corp. 5. FG Bukidnon Power Corporation 6. First Gas Power Corporation 7. First Gen Hydro Power Corporation 8. First Natgas Power Corp. 9. Fresh River Lakes Corp. 10. Green Core Geothermal, Inc. 11. Prime Meridian Powergen Corporation
Visayas | SPC Island Power Corporation | Panay 3 DPP | Echo | 15 | 2026-05-15 | 21:54 |  |  | 2026-05-15 | 23:10 | 1.2667 | Manually shut down unit Echo due to excessive fuel leak at fuel header of cylinder A8. | Diesel | 14 | 2.77 | -11.23 | N/A | N/A | N/A | N/A | Under Korea Electric Power Corporation with affiliations with the following: 1. KEPCO SPC Power Corporation 2. SPC Island Power Corporation 3. SPC Power Corporation
Visayas | SPC Island Power Corporation | Bohol DPP | Unit 4 | 5.52 | 2026-05-15 | 21:50 |  |  | 2026-05-16 | 0:00 | 2.1667 | Forced cut-out due to observed knocking sound at cylinder no.1. | Diesel | 14 | 1.0208 | -12.9792 | BLCI | 16 MW | N/A | N/A
Visayas | Central Negros Power Reliability, Inc. | CENPRI Bunker C-Fired DPP | Unit 2 | 5 | 2026-05-15 | 14:17 |  |  | 2026-05-16 | 20:48 | 30.5167 | DG set unload due to water ingress in lube oil system | Diesel | 14 | 2.2361 | -11.7639 | CENECO | 18.9 MW | N/A | N/A | Under Energreen Power Inter-Island Corp. with affiliations with the following: 1. Central Negros Power Reliability, Inc. 2. Mindoro Harvest Energy Co. Inc.
Visayas | SPC Island Power Corporation | Bohol DPP | Unit 2 | 5.52 | 2026-05-15 | 13:01 |  |  | 2026-05-18 | 1:00 | 59.9833 | Forced outage due to failure to start after several attempts | Diesel | 14 | 3.125 | -10.875 | BLCI | 16 MW | N/A | N/A | Under Korea Electric Power Corporation with affiliations with the following: 1. KEPCO SPC Power Corporation 2. SPC Island Power Corporation 3. SPC Power Corporation
Visayas | SPC Island Power Corporation | Panay 3 DPP | Golf | 15 | 2026-05-15 | 11:11 |  |  | 2026-05-15 | 15:10 | 3.9833 | Manually shutdown unit Golf due to excessive lube oil leak at cracked supply pipe B-bank | Diesel | - | - | - | N/A | N/A | N/A | N/A
Visayas | Toledo Power Company | Carmen DPP | DG 1 | 11.45 | 2026-05-15 | 11:06 |  |  | 2026-05-15 | 14:49 | 3.7167 | DG No. 1 tripped due to engine over speed | Diesel | 14 | 45.4361 | 31.4361 | MERALCO CEBECO III | 73 MW | N/A | N/A | Under Manila Electric Company with affiliations with the following: 1. Excellent Energy Resources, Inc. 2. Cebu Energy Development Corporation 2. Greentech Solar Energy, Inc. 3. Nuevo Solar Energy Corp. 5. Panay Energy Development Corporation 6. Panay Power Corporation 4. PH Renewables, Inc. 5. Powersource First Bulacan Solar Inc. 6. San Buenaventura Power Ltd. Co. 7. Solar Philippines Calatagan Corporation 8. Solar Philippines Tarlac Corporation 9. South Premiere Power Corp. 10. Toledo Power Co.
Visayas | SPC Island Power Corporation | Panay 1 DPP | Unit 5 | 7.44 | 2026-05-15 | 10:31 |  |  | 2026-05-17 | 7:10 | 44.65 | Unable to cut in unit 5 due to observed sudden increase of bearing temperature of main bearing no. 1 | Diesel | 14 | 5.5 | -8.5 | N/A | N/A | N/A | N/A | Under Korea Electric Power Corporation with affiliations with the following: 1. KEPCO SPC Power Corporation 2. SPC Island Power Corporation 3. SPC Power Corporation
Visayas | First Farmers Holding Corporation | FFHC BPP | Unit 1 | 21.76 | 2026-05-15 | 3:07 |  |  | 2026-05-16 | 14:37 | 35.5 | Insufficient cane supply | Biomass | - | - | - | NONESCO / VRESO | 3 MW | N/A | N/A | No other affiliations; Owned majority by Individuals
Visayas | Universal Robina Corporation | Kabankalan BPP | Unit 2 | 16 | 2026-05-15 | 1:20 |  |  | 2026-05-16 | 19:04 | 41.7333 | Heavy turbine fault | Biomass | 7 | 1.92 | -5.08 | N/A | N/A | N/A | N/A | Under JG Summit Holdings, Inc. Group
Visayas | SPC Island Power Corporation | Bohol DPP | Unit 3 | 5.52 | 2026-05-14 | 23:22 |  |  | 2026-05-15 | 2:00 | 2.6333 | Forced outage due to observed fuel leak at cylinder no. 6 | Diesel | 14 | 3.3535 | -10.6465 | BLCI | 16 MW | N/A | N/A | Under Korea Electric Power Corporation with affiliations with the following: 1. KEPCO SPC Power Corporation 2. SPC Island Power Corporation 3. SPC Power Corporation
Visayas | Sunwest Water and Electric Company 2, Inc. | Villasiga HEPP | Unit 2 | 3.6 | 2026-05-14 | 22:00 | TBD |  |  |  | - | Shutdown due to low water yield | Hydroelectric | - | - | - | ANTECO | 8 MW | N/A | N/A | Under Sunwest Group Holding Company, Inc. with affiliations with the following: 1. Sunwest Water and Electric Company 2, Inc. 2. Sunwest Water and Electric Co. (SUWECO), Inc. 3. SUWECO Tablas Energy Corporation
Visayas | Meridian Power Inc. | MPI Bunker C-Fired DPP | DG 8 | 7.059 | 2026-05-14 | 20:05 |  |  | 2026-05-15 | 3:28 | 7.3833 | Water Leak | Diesel | 14 | 2.0028 | -11.9972 | VECO | 70 MW | N/A | N/A | Under Vivant Corporation with affiliations with the following: 1. 1590 Energy Corp. 2. Bukidnonpower Corporation 3. Calamian Islands Power Corp. 4. Cebu Energy Development Corporation 5. Delta P, Inc. and AERSI 6. Isla Norte Power Corporation 7. Meridian Power Inc. 8. Minergy Power Corporation 9. North Bukidnonpower Corporation
Visayas | SPC Island Power Corporation | Panay 3 DPP | Charlie | 13.3 | 2026-05-14 | 18:24 |  |  | 2026-05-15 | 3:50 | 9.4333 | Pulled ut and replace cylinder liner and cylinder head A5 | Diesel | 14 | 11.6 | -2.4 | N/A | N/A | N/A | N/A | Under Korea Electric Power Corporation with affiliations with the following: 1. KEPCO SPC Power Corporation 2. SPC Island Power Corporation 3. SPC Power Corporation
Visayas | SPC Island Power Corporation | Bohol DPP | Unit 3 | 5.52 | 2026-05-14 | 13:01 |  |  | 2026-05-14 | 15:20 | 2.3167 | Forced outage due to observed fuel leak at cylinder no. 1 header supply line | Diesel | 14 | 3.3535 | -10.6465 | BLCI | 16 MW | N/A | N/A
Visayas | SPC Power Corporation | Power Barge 104 | Unit 2 | 8 | 2026-05-14 | 12:56 |  |  | 2026-05-15 | 12:15 | 23.3167 | Unable to cut in due to excessive Exhaust gas leak at Cylinder 5R | Diesel | 14 | 1.2104 | -12.7896 | N/A | N/A | N/A | N/A
Visayas | SPC Island Power Corporation | Panay 3 DPP | Golf | 15 | 2026-05-14 | 8:48 |  |  | 2026-05-14 | 16:10 | 7.3667 | Conducted grounding of surface between engine frame and liner on cylinder A8 | Diesel | - | - | - | N/A | N/A | N/A | N/A
Visayas | Green Core Geothermal, Inc. | Palinpinon 1 GPP | Unit 3 | 37.5 | 2026-05-14 | 2:09 |  |  | 2026-05-15 | 1:20 | 23.1833 | Unit on emergency shutdown to rectify minor sticking issue with the Main Stop Valve | Geothermal | 13.7 | 17.95 | 4.25 | ILECO I CAPELCO | 18 MW 12 MW | N/A | N/A | Under First Gen Corporation with affiliations with the following: 1. Bac-Man Geothermal Inc. 2. EDC Burgos Wind Power Corporation 3. Energy Development Corporation 4. FGP Corp. 5. FG Bukidnon Power Corporation 6. First Gas Power Corporation 7. First Gen Hydro Power Corporation 8. First Natgas Power Corp. 9. Fresh River Lakes Corp. 10. Green Core Geothermal, Inc. 11. Prime Meridian Powergen Corporation
Visayas | Energy Development Corporation | Malitbog Bottoming Cycle | Unit 1 | 16 | 2026-05-14 | 0:07 |  |  | 2026-05-15 | 1:41 | 25.5667 | OEC7 was cut out to replace the erratic hydraulic pump HOP 504 and inspect the excited fan hub bot and nut | Geothermal | 13.7 | 44.36 | 30.66 | BILECO DORELCO LEYECO III LEYECO IV LEYECO V ESAMELCO | 1 MW 2 MW 1 MW 1 MW 8 MW 6 MW | N/A | N/A
Visayas | Meridian Power Inc. | MPI Bunker C-Fired DPP | DG 1 | 7.059 | 2026-05-13 | 13:47 |  |  | 2026-05-13 | 14:46 | 0.98333 | Tripped due to generator bearing high temperature at A side | Diesel | 14 | 1.0125 | -12.9875 | VECO | 70 MW | N/A | N/A | Under Vivant Corporation with affiliations with the following: 1. 1590 Energy Corp. 2. Bukidnonpower Corporation 3. Calamian Islands Power Corp. 4. Cebu Energy Development Corporation 5. Delta P, Inc. and AERSI 6. Isla Norte Power Corporation 7. Meridian Power Inc. 8. Minergy Power Corporation 9. North Bukidnonpower Corporation
Visayas | Meridian Power Inc. | MPI Bunker C-Fired DPP | DG 1 | 7.059 | 2026-05-13 | 12:55 |  |  | 2026-05-13 | 13:14 | 0.31667 | Tripped due to generator bearing high temperature at B side | Diesel | 14 | 1.0125 | -12.9875 | VECO | 70 MW | N/A | N/A
Visayas | SPC Island Power Corporation | Bohol DPP | Unit 1 | 5.52 | 2026-05-13 | 11:46 |  |  | 2026-05-17 | 17:15 | 101.4833 | Unable to Cut-in Due to severe water leak at JCW Header-In of CYL. #8 | Diesel | 14 | 2.0312 | -11.9688 | BLCI | 16 MW | N/A | N/A | Under Korea Electric Power Corporation with affiliations with the following: 1. KEPCO SPC Power Corporation 2. SPC Island Power Corporation 3. SPC Power Corporation
Visayas | Sunwest Water and Electric Company 2, Inc. | Villasiga HEPP | Unit 2 | 3.6 | 2026-05-13 | 11:00 |  |  | 2026-05-14 | 19:00 | 32 | Shutdown due to low water yield | Hydroelectric | - | - | - | ANTECO | 8 MW | N/A | N/A | Under Sunwest Group Holding Company, Inc. with affiliations with the following: 1. Sunwest Water and Electric Company 2, Inc. 2. Sunwest Water and Electric Co. (SUWECO), Inc. 3. SUWECO Tablas Energy Corporation
Visayas | Panay Power Corporation | PPC 4 DPP | DG 1 | 5 | 2026-05-12 | 18:05 | 2026-05-14 | 14:00 | 2026-05-14 | 14:00 | 43.9167 | Unit encountered issues in its generator, resulting in the unavailability of the unit. | Diesel | 14 | 4.53 | -9.47 | N/A | N/A | N/A | N/A | Under Manila Electric Company with affiliations with the following: 1. Excellent Energy Resources, Inc. 2. Cebu Energy Development Corporation 2. Greentech Solar Energy, Inc. 3. Nuevo Solar Energy Corp. 5. Panay Energy Development Corporation 6. Panay Power Corporation 4. PH Renewables, Inc. 5. Powersource First Bulacan Solar Inc. 6. San Buenaventura Power Ltd. Co. 7. Solar Philippines Calatagan Corporation 8. Solar Philippines Tarlac Corporation 9. South Premiere Power Corp. 10. Toledo Power Co.
Visayas | Therma Visayas, Inc. | TVI CFPP | Unit 1 | 176.97 | 2026-05-12 | 16:16 | 2026-08-30 | 23:59 |  |  | - | Steam turbine bearing#1 vibration high | Coal-Fired | 16.9 | 39.2 | 22.3 | CEBECO I INEC VECO AEC NEPC | 2 MW 3 MW 45 MW 39 MW 20 MW | N/A | N/A | Under Aboitiz Equity Ventures, Inc. Group with affiliations with the following: 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc.
Visayas | Meridian Power Inc. | MPI Bunker C-Fired DPP | DG 6 | 7.059 | 2026-05-12 | 15:00 |  |  | 2026-05-12 | 15:45 | 0.75 | Water Leak | Diesel | 14 | 24.2687 | 10.2687 | VECO | 70 MW | N/A | N/A | Under Vivant Corporation with affiliations with the following: 1. 1590 Energy Corp. 2. Bukidnonpower Corporation 3. Calamian Islands Power Corp. 4. Cebu Energy Development Corporation 5. Delta P, Inc. and AERSI 6. Isla Norte Power Corporation 7. Meridian Power Inc. 8. Minergy Power Corporation 9. North Bukidnonpower Corporation
Visayas | Central Negros Power Reliability, Inc. | CENPRI Bunker C-Fired DPP | Unit 1 | 5 | 2026-05-12 | 12:51 |  |  | 2026-05-12 | 14:21 | 1.5 | DG Set forced outage due to abnormal sound at Cylinder A5 | Diesel | 14 | 3.0181 | -10.9819 | CENECO | 18.9 MW | N/A | N/A | Under Energreen Power Inter-Island Corp. with affiliations with the following: 1. Central Negros Power Reliability, Inc. 2. Mindoro Harvest Energy Co. Inc.
Visayas | Sunwest Water and Electric Company 2, Inc. | Villasiga HEPP | Unit 2 | 3.6 | 2026-05-12 | 1:00 |  |  | 2026-05-13 | 8:00 | 31 | Shutdown due to low water yield | Hydroelectric | - | - | - | ANTECO | 8 MW | N/A | N/A | Under Sunwest Group Holding Company, Inc. with affiliations with the following: 1. Sunwest Water and Electric Company 2, Inc. 2. Sunwest Water and Electric Co. (SUWECO), Inc. 3. SUWECO Tablas Energy Corporation
Visayas | First Farmers Holding Corporation | FFHC BPP | Unit 1 | 21.76 | 2026-05-12 | 0:00 |  |  | 2026-05-13 | 18:38 | 42.6333 | Cane accumulation | Biomass | - | - | - | NONESCO / VRESO | 3 MW | N/A | N/A | No other affiliations; Owned majority by Individuals
Visayas | SPC Power Corporation | Power Barge 104 | Unit 3 | 8 | 2026-05-11 | 18:40 | 2026-05-21 | 23:59 |  |  | - | Auto tripped unit due to Turbo charger lube oil inlet pressure low | Diesel | 14 | 7.6271 | -6.3729 | N/A | N/A | N/A | N/A | Under Korea Electric Power Corporation with affiliations with the following: 1. KEPCO SPC Power Corporation 2. SPC Island Power Corporation 3. SPC Power Corporation
Visayas | Panay Energy Development Corporation | PEDC CFTPP | Unit 3 | 150.025 | 2026-05-06 | 16:15 | N/A | N/A |  |  | - | Still under investigation | Coal-Fired | 16.9 | 19.4375 | 2.5375 | ILECO II PECO AKELCO | 10 MW 65 MW 12 MW | N/A | N/A | Under Manila Electric Company with affiliations with the following: 1. Excellent Energy Resources, Inc. 2. Cebu Energy Development Corporation 2. Greentech Solar Energy, Inc. 3. Nuevo Solar Energy Corp. 5. Panay Energy Development Corporation 6. Panay Power Corporation 4. PH Renewables, Inc. 5. Powersource First Bulacan Solar Inc. 6. San Buenaventura Power Ltd. Co. 7. Solar Philippines Calatagan Corporation 8. Solar Philippines Tarlac Corporation 9. South Premiere Power Corp. 10. Toledo Power Co.
Visayas | Central Azucarera De San Antonio, Inc. | CASA BPP | Unit 2 | 8 | 2026-05-06 | 12:06 |  |  | 2026-05-19 | 10:29 | 310.3833 | Low exhaust steam pressure requirements of processhouse, insufficient sugarcane supply | Biomass | 7 | 66.1021 | 59.1021 | N/A | N/A | N/A | N/A | Under Chan Group with affiliations with the following: 1. Central Azucarera De Bais, Inc. 2. Central Azucarera De San Antonio, Inc.
Visayas | Biscom Inc. | BISCOM BPP | Unit 1 | 30 | 2026-04-27 | 21:40 |  |  |  |  | - | Low level of condensate water supplying TES boiler | Biomass | - | - | - | N/A | N/A | N/A | N/A | No other affiliations; Owned majority by Individuals
Visayas | Energy Development Corporation | Upper Mahiao GPP | Unit 3 | 37.36 | 2026-04-27 | 13:42 |  |  | 2026-05-16 | 7:06 | 449.4 | UMPP Unit 3 was cut-out for reserve shutdown due to insufficient high pressure steam supply. | Geothermal | 13.7 | 103.17 | 89.47 | BILECO DORELCO LEYECO III LEYECO IV LEYECO V ESAMELCO | 1 MW 2 MW 1 MW 1 MW 8 MW 6 MW | N/A | N/A | Under First Gen Corporation with affiliations with the following: 1. Bac-Man Geothermal Inc. 2. EDC Burgos Wind Power Corporation 3. Energy Development Corporation 4. FGP Corp. 5. FG Bukidnon Power Corporation 6. First Gas Power Corporation 7. First Gen Hydro Power Corporation 8. First Natgas Power Corp. 9. Fresh River Lakes Corp. 10. Green Core Geothermal, Inc. 11. Prime Meridian Powergen Corporation
Visayas | Energy Development Corporation | Mahanagdong Topping Cycle - Site A | Unit 1 | 7 | 2026-04-05 | 14:48 | TBD |  |  |  | - | MATP (MGATC) OEC 2 tripped with Generator Non Drive Bearing High Temperature indication | Geothermal | 13.7 | 71.19 | 57.49 | BILECO DORELCO LEYECO III LEYECO IV LEYECO V ESAMELCO | 1 MW 2 MW 1 MW 1 MW 8 MW 6 MW | N/A | N/A
Visayas | Energy Development Corporation | Upper Mahiao GPP | Unit 4 | 37.36 | 2026-05-18 | 2:32 | TBD |  |  |  | - | UMPP Unit 4 is on reserved shutdown due to insufficient steam supply. | Geothermal | 13.7 | 64.87 | 51.17 | BILECO DORELCO LEYECO III LEYECO IV LEYECO V ESAMELCO | 1 MW 2 MW 1 MW 1 MW 8 MW 6 MW | N/A | N/A
Visayas | Therma Visayas, Inc. | TVI CFPP | Unit 2 | 176.97 | 2026-03-24 | 21:17 | 2026-08-22 | 23:59 |  |  | - | STG bearing #1 vibration high | Coal-Fired | 13.7 | 69.99 | 56.29 | CEBECO I INEC VECO AEC NEPC | 2 MW 3 MW 45 MW 39 MW 20 MW | N/A | N/A | Under Aboitiz Equity Ventures, Inc. Group with affiliations with the following: 1. Aboitiz Solar Power Inc. 2. AP Renewables, Inc. 3. Apo Agua Infrastructure, Inc. 4. CBK Power Company Limited 5. Cebu Energy Development Corporation 6. Cotabato Light & Power Company 7. East Asia Utilities Corporation 8. Excellent Energy Resources, Inc. 9. GNPower Dinginin Ltd. Co. 10. GNPower Mariveles Energy Center Ltd. Co. 11. Hedcor Bukidnon, Inc. 12. Hedcor Sabangan, Inc. 13. Hedcor Sibulan, Inc. 14. Hedcor Tudaya, Inc. 15. Hedcor Inc. 16. Pagbilao Energy Corporation 17. PV Sinag Power Inc. 18. RE Resources, Inc. 19. Republic Cement & Building Materials, Inc. 20. San Carlos Sun Power 21. SN Aboitiz Power Benguet, Inc. 22. SN Aboitiz Power Magat, Inc. 23. South Premiere Power Corp. 24. SPI Power Incorporated 25. Therma Luzon, Inc. 26. Therma Marine, Inc. 27. Therma Mobile, Inc. 28. Therma South Inc. 29. Therma Visayas, Inc.
Visayas | Sunwest Water and Electric Company 2, Inc. | Villasiga HEPP | Unit 1 | 3.6 | 2026-03-21 | 13:00 | TBD |  |  |  | - | Shutdown due to low water yield | Hydroelectric | - | - | - | ANTECO | 8 MW | N/A | N/A | Under Sunwest Group Holding Company, Inc. with affiliations with the following: 1. Sunwest Water and Electric Company 2, Inc. 2. Sunwest Water and Electric Co. (SUWECO), Inc. 3. SUWECO Tablas Energy Corporation
Visayas | Energy Development Corporation | Mahanagdong GPP | Unit 4 | 24 | 2025-12-02 | 17:58 | 2026-06-02 | 24:00 |  |  | - | MAPP (MGAPP) Unit 4 (Binary) tripped with speed governor trip indication. | Geothermal | 13.7 | 138 | 124.3 | BILECO DORELCO LEYECO III LEYECO IV LEYECO V ESAMELCO | 1 MW 2 MW 1 MW 1 MW 8 MW 6 MW | N/A | N/A | Under First Gen Corporation with affiliations with the following: 1. Bac-Man Geothermal Inc. 2. EDC Burgos Wind Power Corporation 3. Energy Development Corporation 4. FGP Corp. 5. FG Bukidnon Power Corporation 6. First Gas Power Corporation 7. First Gen Hydro Power Corporation 8. First Natgas Power Corp. 9. Fresh River Lakes Corp. 10. Green Core Geothermal, Inc. 11. Prime Meridian Powergen Corporation
Visayas | SPC Island Power Corporation | Panay 1 DPP | Unit 2 | 7.44 | 2025-09-14 | 10:11 | TBD |  |  |  | - | Unable to start due to loss of excitation voltage and abnormal sound at generator | Diesel | 14 | 139.98 | 125.98 | N/A | N/A | N/A | N/A | Under Korea Electric Power Corporation with affiliations with the following: 1. KEPCO SPC Power Corporation 2. SPC Island Power Corporation 3. SPC Power Corporation
Visayas | Amlan Hydroelectric Power Corporation | Amlan HEPP | Unit 2 | 0.4 | 2025-08-18 | 17:08 | TBD |  |  |  | - | Low water level | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A | Under Philippine Potamis Hydro Power Corp. with affiliations with the following: 1. Amlan Hydroelectric Power Corporation 2. Catuiran Hydropower Corporation 3. Sta. Clara Power Corporation
Visayas | Amlan Hydroelectric Power Corporation | Amlan HEPP | Unit 1 | 0.4 | 2025-08-14 | 12:35 | TBD |  |  |  | - | Low water level | Hydroelectric | - | - | - | N/A | N/A | N/A | N/A
Visayas | North Negros Biopower, Inc. | NNBP BPP | Unit 1 | 26.256 | 2025-11-25 | 12:00 | Expected in Q2 2026 |  |  |  | - | Shutdown due to insufficient fuel following the end of harvest season | Biomass | 7 | 138 | 131 | N/A | N/A | N/A | N/A | Under Thomaslloyd CTI Asia Holdings PTE. LTD with affiliations with the following: 1. North Negros Biopower, Inc. 2. San Carlos Biopower, Inc. 3. South Negros Biopower, Inc.
Visayas | South Negros Biopower, Inc. | SNBP BPP | Unit 1 | 26.256 | 2025-04-28 | 9:26 | Expected in Q2 2026 |  |  |  | - | Shutdown due to insufficient fuel | Biomass | 7 | 138 | 131 | N/A | N/A | N/A | N/A
Visayas | Energy Development Corporation | Upper Mahiao GPP | Unit 2 | 37.36 | 2024-10-23 | 8:25 | Under Decommissioning, with LOC dated 05 Mar 2026, effectivity is on 30 November 2026 |  |  |  | - | Unit offline as UMPP was put on Total Plant Shutdown to facilitate the immediate inspection of its Ormat Energy Converter (OEC) air-cooled condensers. For Decommissioning with ongoing evaluation of DOE (End of economic life) | Geothermal | 13.7 | 138 | 124.3 | BILECO DORELCO LEYECO III LEYECO IV LEYECO V ESAMELCO | 1 MW 2 MW 1 MW 1 MW 8 MW 6 MW | N/A | N/A | Under First Gen Corporation with affiliations with the following: 1. Bac-Man Geothermal Inc. 2. EDC Burgos Wind Power Corporation 3. Energy Development Corporation 4. FGP Corp. 5. FG Bukidnon Power Corporation 6. First Gas Power Corporation 7. First Gen Hydro Power Corporation 8. First Natgas Power Corp. 9. Fresh River Lakes Corp. 10. Green Core Geothermal, Inc. 11. Prime Meridian Powergen Corporation
Visayas | Energy Development Corporation | Upper Mahiao GPP | Unit 1 | 37.36 | 2024-10-23 | 8:21 | Under Decommissioning, with LOC dated 05 Mar 2026, effectivity is on 30 November 2026 |  |  |  | - | Unit offline as UMPP was put on Total Plant Shutdown to facilitate the immediate inspection of its Ormat Energy Converter (OEC) air-cooled condensers. For Decommissioning with ongoing evaluation of DOE (End of economic life) | Geothermal | 13.7 | 138 | 124.3 | BILECO DORELCO LEYECO III LEYECO IV LEYECO V ESAMELCO | 1 MW 2 MW 1 MW 1 MW 8 MW 6 MW | N/A | N/A
Visayas | San Carlos Biopower, Inc. | SCBP BPP | Unit 1 | 19.99 | 2025-11-25 | 12:00 | Expected in Q2 2026 |  |  |  | - | The plant is temporarily offline while funding efforts are being undertaken to resume fuel collection and return the plant to full operation | Biomass | 7 | 138 | 131 | MERALCO | 20 MW | N/A | N/A | Under Thomaslloyd CTI Asia Holdings PTE. LTD with affiliations with the following: 1. North Negros Biopower, Inc. 2. San Carlos Biopower, Inc. 3. South Negros Biopower, Inc.
Visayas | Victorias Milling Company Inc. | VMCI BPP | Unit 1 | 23 | 2024-04-21 | 16:20 | TBD |  |  |  | - | NGCP tagged on outage since 2024 April. Upon verification, operating on house load since 24 April 2024 | Biomass | 7 | 139.23 | 132.23 | N/A | N/A | N/A | N/A | Under LT Group, Inc. with affiliations with the following: 1. Absolut Distillers, Inc. 2. Victorias Milling Company, Inc.
Visayas | Hawaiian Philippine Company | HPC BPP | Unit 1 | 8 | 2023-11-12 | 20:00 | Reported as Reserved Shutdown |  |  |  | - | Unit is on standby since 2023 due to single boiler setup for both Unit 1 and 2 | Biomass | - | - | - | N/A | N/A | N/A | N/A | Under Kanlaon Loney Holdings, Inc.
Visayas | San Carlos Bioenergy, Inc. | SCBI BPP | Unit 1 | 8.3 | 2022-05-26 | 0:00 |  |  |  |  | - | Not operational since May 2022 (Generating Facility is For Sale) | Biomass | N/A | N/A | No valid COC | MERALCO | 20 MW | N/A | N/A | Under Roxas Holdings, Inc. with affiliations with the following: 1. Central Azucarera Don Pedro, Inc. 2. San Carlos Bioenergy, Inc.
Visayas | Bohol I Electric Cooperative, Inc. | Janopol MHEPP | Unit 1 | 2.64 | 2021-12-31 | 0:00 |  |  |  |  | - | Not operational since December 2021 due to Typhoon Odette | Hydroelectric | N/A | N/A | No valid COC | N/A | N/A | N/A | N/A | No affiliations; Under a Cooperative Arrangement
Visayas | Bohol I Electric Cooperative, Inc. | Janopol MHEPP | Unit 2 | 2.64 | 2021-12-31 | 0:00 |  |  |  |  | - | Not operational since December 2021 due to Typhoon Odette | Hydroelectric | N/A | N/A | No valid COC | N/A | N/A | N/A | N/A
Note on Q12: Rheena Bianca R. Villeno: as of week 19
Note on H14: Justin Roxas From OER PO
Note on H15: As per Sir Pastor
Note on Q16: As of Week 19
Note on Q21: Jean Rose E. Villagracia: As of 10 May 2026
Note on Q23: As of Week 19
Note on Q25: As of Week 19
Note on Q31: As of Week 19
Note on C33: Frank James: Not included in the SIN
Note on Q35: As of Week 19
Note on C40: Frank James: Not included in the SIN
Note on C41: Frank James: Not included in the SIN
Note on Q42: As of Week 19
Note on C46: Frank James: Not included in the SIN
Note on H50: As per Engr. Tutor
Note on Q51: Rheena Bianca R. Villeno: on going outage/ as of May 18, 23:59
Note on H60: Still checking on their Maintenance Team for its Estimated D/T of resumption as per PDPP1
Note on C65: ENGR. JANRECK CRIBE: Under Decommissioning with LOC dated 05 Mar 2026, effective 30 November 2026
Note on C66: ENGR. JANRECK CRIBE: Under Decommissioning with LOC dated 05 Mar 2026, effective 30 November 2026.
Note on H68: ERC IED GenCo: Standby Unit due to Transformer Work as per Sir Joe of VMCI
Note on M70: ENGR. JANRECK CRIBE:

## Luzon Marginal Plants
LUZON
DATE | HOUR | PRICE (PhP/MWh) | ALERT | MARKET INTERVENTION | Customer Indicative AP (PhP/MWh) | Marginal Plant during Alerts
2026-05-13 | 15 | AP | RED | YES | 5632.4118
| 16 | AP | RED | YES | 6844.1718
| 17 | AP | RED | YES | 8094.7437
| 18 | AP | RED | YES | 9226.7667
| 19 | AP | RED | YES | 16227.6963
| 20 | AP | RED | YES | 9671.008
| 21 | AP | RED | YES | 7251.7299
| 22 | AP | RED | YES | 7765.1888
| 23 | AP | RED | YES | 8266.6446
| 24 | AP | RED | YES | 5601.431
2026-05-14 | 15 | 32000 | YELLOW | NO |  | Sta. Rita 1
| 16 | AP | RED | YES | 8575.8303
| 17 | AP | RED | YES | 9399.5595
| 18 | AP | RED | YES | 9449.264
| 19 | AP | RED | YES | 13810.7741
| 20 | AP | RED | YES | 9099.1223
| 21 | AP | RED | YES | 9090.6832
| 22 | AP | RED | YES | 7213.9116
| 23 | AP | RED | YES | 5233.1514
2026-05-15 | 14 | 32000 | YELLOW | NO |  | Sta. Rita 1 Bauang 1
| 15 | AP | RED | YES | 9230.2474
| 16 | AP | RED | YES | 9361.8661
| 17 | AP | RED | YES | 11361.9439
| 18 | AP | RED | YES | 11988.6383
| 19 | AP | RED | YES | 15957.7483
| 20 | AP | RED | YES | 16265.6891
| 21 | AP | RED | YES | 14986.19
| 22 | AP | RED | YES | 13817.57
| 23 | 32000 | RED | NO |  | Bauang 1
| 24 | 21180.27 | YELLOW | NO |  | Carmen DPP Units 1-3

## Visayas Marginal Plants
VISAYAS
DATE | HOUR | PRICE (PhP/MWh) | ALERT | MARKET INTERVENTION | Customer Indicative AP (PhP/MWh) | Marginal Plant during Alerts
2026-05-13 | 16 | AP | RED | YES | 11980.0321
| 17 | AP | RED | YES | 8094.7437
| 18 | AP | RED | YES | 9226.7667
| 19 | AP | RED | YES | 16227.6963
| 20 | AP | RED | YES | 9671.008
| 21 | AP | RED | YES | 7251.7299
| 22 | AP | RED | YES | 7729.3138
| 23 | 32000 | YELLOW | NO |  | Southern Negros BESS
| 24 | 32000 | YELLOW | NO |  | Southern Negros BESS, Bohol DPP Unit 4, Bohol In-island DPP
2026-05-14 | 16 | AP | RED | YES | 8671.627
| 17 | AP | RED | YES | 9399.5595
| 18 | AP | RED | YES | 9449.264
| 19 | AP | RED | YES | 13810.7741
| 20 | AP | RED | YES | 9099.1223
| 21 | AP | RED | YES | 9090.6832
| 22 | AP | YELLOW | YES | 7135.5291
| 23 | 32000 | YELLOW | NO |  | GNPK Units 1-3, Magdum Bunker Diesel Units 1 and 3, Therma Mobil 1 Unit 2
2026-05-15 | 15 | 32000 | YELLOW | NO |  | Iligan DPP Units 1,8, and 10, Mapalad DPP, Sulzer DPP, Wartzila DPP, Villanueva BESS
| 16 | 32000 | RED | NO |  | King - Jimenez Units 1-2, Ilijan DPP Units 7-10, PACERM, Villanueva BESS, Therma Mobil 2 Unit 2, Digos DPP
| 17 | AP | RED | YES | 9217.9278
| 18 | AP | RED | YES | 11988.6383
| 19 | AP | RED | YES | 15957.7483
| 20 | AP | RED | YES | 16265.6891
| 21 | AP | RED | YES | 14986.186
| 22 | 32000 | RED | NO |  | WMPC Unit 10, GNPK Units 3-4, Therma Mobil 2 Unit 2
| 23 | 32000 | RED | NO |  | GNPK Units 3-4, Therma Mobil 2 Unit 2, Therma Mobil 1 Unit 2
| 24 | 21180.7 | YELLOW | NO |  | Bohol DPP Unit 3
2026-05-16 | 18 | 32000 | YELLOW | NO |  | Kabankalan BESS, Southern Negros BESS, Power Barge 101 Units 1-4
| 19 | 32000 | YELLOW | NO |  | WMPC Units 3 and 7, GNPK Unit 2, Therma Mobil 2 Unit 2, Therma Mobil 1 Unit 2, Magdum Bunker Diesel Unit 3
| 20 | 32000 | YELLOW | NO |  | GNPK Units 1-4, Therma Mobil 2 Unit 2, Therma Mobil 1 Unit 2
| 21 | 32000 | YELLOW | NO |  | GNPK Units 1-4
| 22 | 20931.28 | YELLOW | NO |  | Kabankalan BESS, Bohol In-island DPP, Power Barge 101 Units 1-4
2026-05-18 | 16 | 32000 | YELLOW | NO |  | Jasaan BESS, NBPC, PACERM, Therma Mobil 2 Unit 1, Digos DPP
| 17 | 32000 | YELLOW | NO |  | Ilijan DPP Unit 10, PACERM, PeakPower San Francisco Unit 2, Therma Mobil 2 Unit 1, Digos DPP
| 18 | 32000 | YELLOW | NO |  | WMPC Units 1-2, 5, and 8, GNPK Units 3-4, Magdum Bunker Diesel Unit 1, Digos DPP
| 19 | 32000 | YELLOW | NO |  | PeakPower San Francisco Unit 1, Therma Mobil 2 Unit 1, Digos DPP
| 20 | 32000 | YELLOW | NO |  | Ilijan DPP Units 7-8 and 10-12, Wartzila DPP, PeakPower San Francisco Unit 2
| 21 | 32000 | YELLOW | NO |  | GNPK Units 3-4, Ilijan DPP Units 5-6